Exquisite Heat Prom program sheet

Factory Software settings:  If you desire a different setting cross out the factory setting and write in your desired setting. Please fill in all contact information so we can call and speak to you.  You can copy and paste this information to e-mail, (preferred) or  print and mail to Exqheat Software Settings, 172 Foshay Ave. Pleasantville, NY 10570.   e-mail  Exqheat@prodigy.net  Tel: 914-588-4791 to discuss features.

Exqheat Menu

Temperature control menu hot water boiler

1) Analysis Interval               =   60 min.   reads thermostat status every second.

2) System Startup Delay        =    1 min.   (do not change)

3) Demand Ratio Ideal           =  70 %  circulation rate  (60-85%)

4) Actual Demand Ratio Min =  10 % resets to startup temp.  See item 5)

5) Startup Temperature          = 150 deg. (150-180)________________

6) Deg Change Increment      =     3 deg.  (2-5 range) ______________

7) Range Differential             =    15 deg. (15-20 range) ____________

8) High Temp Absolute         =  200 deg. (170-210 range)__________

Will not allow high limit to calculate above this temp.

9) High Temp Safety             =  250 deg. (220-275 range)__________

Will trigger alarm relay and resets to start up temp.

10)  Low Temp Absolute        =  135 deg. (90-150 range) ___________

Will not allow low limit to calculate below this limit.

11)  Low Temp Safety            =    50 deg.  50-75 range) _____________

Will trigger alarm relay and reset to start up.

12) Temperature Averaging    =     5 sec.

13) Thermostat Polarity           =    1 or 0   (use jumper provided on board)

14) Hot Water Low Temp       =  130 deg F. (120-150 range)____________

15)  Cold Start Mode              =   1 ON or  Off   ( Off if Domestic HW from boiler)

Time control menu  Steam Boilers

1) Analysis Interval                 =   60 min. reads thermostat status every second._______

2) System Startup Delay           =    1 min._____________________________________

3) Demand Ratio Ideal             =   60 % time thermostat is calling for heat.___________

4) Actual Demand Ratio Min   =   10 % back to start up on time. See 5)_____________

5) Startup On Time                   =   90 min._____________________________________

6) Increment Factor                   =    3 min._____________________________________

7) Max On Time                        = 120 min.____________________________________

8) Min On Time                         =   15 min._____________________________________

9) Min Off Time                        =   15 min._____________________________________

10) High Temp Safety                = 250 deg.____________________________________

11) Low Temp Safety                 =   50 deg.______________________________________

12) Temperature Averaging        =   5 sec. ( does not change)

13) Thermostat Polarity               =   1 or 0 ___to be determined at install- Jumper #2

14) Hot Water Low Temp         =  130  deg.______________________________________

15) “Time Off “ ratio %              = 30%   Proportioned “Time Off “ based on “Time On”.

Please complete all information needed in order to communicate:      Today’s date:

Name:

Address:

Town:

State:                           Zip code:

Tel     Area code:            Tel#         fax:        Cell:

E-mail:

Exqheat model from the green circuit board.       Date and REV #

Serial number on the board:  this will be hand scripted on the back of the board.

Now save this form so you can use it over and over.

Rev. 11/26/08